- Bruce Lung:	To our webinar on Getting Started with Water Efficiency at Manufacturing Facilities. My name is Bruce Long, and I'm with the Oakridge and Associated Universities. I'm a fellow here at the U.S. Department of Energy working on the Better Plants Program. I'm going to introduce Prakash Rao a little later on in the webinar, but I wanted to thank you all for coming today. I think this is a tremendously important topic, and we're glad to see that y'all are very interested in it. I think it's going to be very impactful and valuable for you.

- The way that we're going to work this webinar is, traditionally, people wait until the end and then they submit questions, but we encourage you to submit questions as the webinar is ongoing, and we're going to pause at certain key junctures, and then ask folks if there are any questions or any comments anyone would like to throw out. So, without waiting too much longer, I'm going to go ahead and get started, and then we'll go as we get along.

- Okay, so today's agenda, we're going to start with an overview of the Better Plants or Better Buildings, Better Plants Program, and then we're going to start getting pretty heavily into the topic of water management. This will include everything from setting and tracking water intensity targets, some example of how to do this, as well as a lot of water efficiency measures. Then we're going to do a deep dive on some of the major industrial systems that are affected by water consumption. You'll see here that includes pumping systems, cooling towers and steam.

- Then we're going to have some other resources to show you guys. This is going to be a fairly lengthy slide deck, so we're going to try to move through it efficiently, but as completely as possible. So, just a quick overview, and I'm sorry if some of you all have already seen this, but we wanted to get everybody up on the same page on this. The Better Buildings, Better Plants Program is a voluntary energy efficiency program oriented towards industrial-scale energy users, particularly manufacturers.

- Basically, partners join the program. They commit to a long-term energy intensity goal reduction of 25 percent over ten years, and in exchange for that, they get the full portfolio of technical assistance and resources from the DOE's vast manufacturing office. That will include everything from setting up a baseline, access to trainings, access to free assessments and combined heat and power, assessments on everything like that as well as some energy management tools and other benefits.

- We also provide a lot of recognition for stepping up and joining this program and some networking opportunities with your peers to understand what has worked in their settings. There are two levels to our program. The main level is the program level in which you come in and you do all the stuff, and you get all the technical assistance.

- The challenge level is also for companies that really want a little more publicity and positive engagement. They commit to sharing some data with us, and we represent it publicly. They also participate in a couple of case studies. So, for that, they get additional recognition and speaking opportunities. But the bottom line is that the focus of the program is to enhance productivity, cost savings, and competitiveness.

- Just to give you a quick overview of where we are and where we've come from, we started in 2009. The program had a slightly different name back then with about 46 partners, and we've grown to 190 today with about 11.5 percent of the U.S. manufacturing footprint. Last year was kind of a big year for us with 33 new partners as well as 10 goal achievers. So, you can see that it's very possible it'll meet the 25 percent goal even before the 10 years is up.

- This slide right here gives you an idea of all the organizations that have joined at the challenge level. So, you'll see some big names like Nissan, Ford, 3M, Eastman Chemical, but also some water and wastewater treatment agencies like Victor Valley Wastewater Reclamation Association, Bucks County Water and Sewer Agency, and a few others. We've seen that the water and wastewater treatment agency has really taken to the program.

- One of the main avenues of technical support is what we call a Technical Account Manager, and for each partner, we basically assign one of these TAMs. The TAMs are engineers with deep knowledge and understanding of industrial-scale energy consuming applications and have solutions to help improve energy performance in those applications. So, each partner will be assigned a TAM, and that TAM will be with you throughout the partnership period, ten years or however long it is.

- The TAMs are integrally involved throughout each partner's participation in events. Everything from generating baselines to arranging trainings and recognition as well as assessments. You'll see there are several approaches to doing the baseline, and they can help you with each one. The other thing that the TAMs will help you do is develop a roadmap for achieving the goals because some people don't know how to get from A to Z. They're not going to tell you what equipment to buy or anything like that, but they can help you understand how to get there so that the process is not quite as daunting.

- A quick note on our in-plant trainings. This is basically the workforce development element of the Better Plants programs. These trainings include everything from short energy assessment and field demonstrations to how to perform an assessment on an industrial system within your plants. As you can see, we offer training on a variety of topics. We've recently added Energy Treasure Hunt Exchanges. We're adding Industrial Refrigeration, Strategic Energy Management, and then Energy Efficiency for Water and Wastewater Treatment.

- As you can see, since 2011, we've had about 850 participants and identified over 3 trillion BTUs and $14 million in energy savings up to 2015. So, we're still tabulating the savings up to today. We also have some pre-in-plant training webinars that happened before each training, and we're in the process of transcribing those webinars so you can see them online and get a sense of what you'll get if you decide to either host or attend one of these trainings.

Now, I want to just take a quick second to focus on the supply chain initiative, as a number of you on the webinar today are in this initiative. Basically, we offer the possibility for companies to sponsor one of these initiatives, and what happens is they'll introduce us to their suppliers. We offer the chance to join, and then another one of the suppliers will come in in a cohort.

Your TAM will still deal with you on an individual basis, but for our purposes, we look at these as cohorts that belong or that work with a particular partner. They get the same level of priority and access to our technical assistance and recognition, but we also give them some more tailored resources like this webinar as well as some other webinars that you'll see after this or even before this.

One of the things that our cohort members get are access, priority access to audits from the industrial assessment centers. If you're not familiar with those, this is a network of about two dozen universities around the country that offer mechanical and electrical and other engineering divisions. They'll come out to your plant with a professor and several students, and they'll perform a free energy assessment for you. It's been very successful and very popular among our supply chain.

A number of these industrial assessment centers can also offer ideas and assessments on water use and wastewater treatment efficiency. Then, again, we also like to have in these webinars and other forms, the opportunity for you to learn from your peers.

One quick initiative I'll mention here is this year we're embarking on a Technology Transfer Initiative in which we can leverage assets of the Oakridge National Lab as well as some of the other national labs in the country to introduce our partners to emerging technologies and innovation and research. It's also a good way to introduce our partners to the labs so that if they want to collaborate on research efforts, they'll understand how to do it, who to work with, and what the modalities are and all that kind of thing. So, that's going to be an important thing probably going forward.

Additionally, one thing that's kind of a part of this technology transfer initiative is the ability to borrow diagnostic equipment from Oakridge National Lab. Basically, it's kind of like the AutoZone model where you go to AutoZone and you borrow some kind of tool to help you change your oil or check your battery, that kind of thing. We provide a variety of diagnostic tools, everything from amp meters to flow meters for free. We pay for the shipping going to and coming back for up to four weeks. Your TAM can also give you some tips on how to use them.

So, it's something we've just started, and we've had some good uptake so far, but we're hoping that it will enable the partners to be able to assess the individual systems themselves, and then be able to understand what they can do, what additional equipment they need, and maybe they'll be able to buy their own equipment and do it on a continuing basis.

A couple of things as I'm wrapping up, just wanted to make a plug for our annual summit coming up in a couple of weeks now. The Better Buildings Summit is an event here in Washington, D.C. where we get up to 1,000 people coming in from all sectors: industrial, commercial, retail, schools, hospitals, all that – that are part of the larger Better Buildings Program to share experiences, solutions, and to learn from one another. We definitely have a lot of sessions in which people will share their experiences. But we also have opportunities in which an expert will be sitting on the panel, and they'll frame a particular topic like sub metering and how various end users in energy can benefit from them.

We also have an Ask-the-Expert feature that you don't have to see in some conferences where you can speak one-on-one with an expert in a particular area. In fact, our speaker on water is going to be one of those experts at this year's Better Buildings Summit. So, registration is open, and we encourage and all to come. We still have space, and we hope to see some of you all there.

So, the last thing that I'll mention is what we call the Better Buildings Solutions Centers. This is our main online platform. You can see the link there at the bottom. This is where we have all the solutions, all the partners listed, all the different initiatives that we have. There's a new item on here called the Financing Navigator where you can actually search for potential funders for your energy efficiency projects. So, we hope that's a good resource. We've gotten a lot of compliments and hits on it, and we hope that's something that you'll be able to use as well.

Let me stop here and see if we have any questions just on the basic Better Plants Program. Okay, hearing none. I don't know if any are coming in through the chat feature or anything like that, but we'll go head and proceed unless, Ray, is there anything else coming in? Okay, good. So, what we'll do is if you want to go ahead, and I can keep my screen open and then just advance the slides, or do you want to try and share it with Prakash?

Ray:	Either works for me

- Bruce Lung:	Okay. Why don't I go ahead, and I'll advance the slides and that way we won't have to try to play around.

Ray:	Sure thing.

- Bruce Lung:	So, it's my pleasure to introduce Dr. Prakash Rao to you today. Dr. Prakash Rao is a Principal Scientific Engineering Associate within the Energy Technologies Division at Lawrence Berkeley National Laboratory in Berkeley, California. He's also known as our water guru. Dr. Rao conducts research and analysis into the potential for reducing the energy consumption and water use impacts of the US manufacturing sector while maintaining its productivity. To this end, Dr. Rao also assists in the development of related technical assistance and deployment activities.

- Dr. Rao received his doctorate in Mechanical and Aerospace Engineering from Rutgers University and a bachelor of Mechanical Engineering from Carnegie Mellon University. So, Prakash, let me know when you want to start, and we'll get started.

Prakash Rao:	Sure, thanks, Bruce. I'm happy to be here today and happy to spend this morning or afternoon, wherever you are, talking about a topic that I think is very important. Next slide please. So, I thought we would start off a little bit at a high level to give some context. How does the U.S. use water? On the left here, you can see that we've broken our water use in the United States by individual sectors. Clearly, thermoelectric, which is power plant cooling and agriculture, which is for food and crops growing, dominate water use in the United States, and manufacturing is about 6 percent.

However, there is an interesting caveat here. In my state right now, California, we recently had water curtailments, 25 percent mandated, and thermoelectric and ag were excluded. So, when you take out thermoelectric and ag, manufacturing shares of water use in the United States rises significantly and it becomes 31 percent. Interestingly enough, and to dive a little bit deeper into the number, where do manufacturers get their water just by and large across the United States? The vast majority of them do not actually purchase it from a municipality. They get it from what's called self-supplied sources.

Here, the inference that we take away is that, "Well, if you're not paying for water, it's likely there's not a lot of incentive to conserve it." So, that means there's a lot of opportunity on the floor. Lastly, I want to point out this one bullet at the bottom about consumptive use. It's a topic well touch on a little bit later where 15 percent of all manufacturing water use is what's called consumptive. So, if you think about how you use water, in many, many, many, many cases you just return it back to the sewer. You return it back to the river, to the lake, wherever you got it from, and the next guy down the line can then use that water for their own purposes.

So, you're not really removing any water for the local area. Consumptive use is a little bit different. Consumptive use is a little bit different. Consumptive use is that portion of that water that, let's say, you evaporate, turns into a cloud, and flies off to who knows where. It goes in your product. Maybe if you're a soft drink bottler, it's being shipped out around the world, or some other use where that water is not actually returning to the watershed. That's called consumptive use.

That's a really critical water use to track because that's the one if we're doing water management for sustainability purposes and environmental and protection purposes, consumptive use impacts your watershed more so than non-consumptive use. Next slide, please.

So, just little bit high-level benefits of water management and challenges. I think you all are on this webinar right now, so clearly, you understand the benefits of water management. But just at a high level, the couple of things that we see is operational resiliency and future growth. It's very forward thinking. So, if you are a good steward of water, if you are using as little water as you can as possible, you're being as conservative and efficient with it, you're better off for planning in the future.

So, should there be curtailment, should there be mandate, should there be spikes in water prices, your facility will not be as impacted and production can continue as normal. On a higher level, if you operate multiple facilities across the country and you know that all your facilities are operating very efficiently with water, that's one less thing you really have to worry about when you're thinking about where do you set your next facility? Where do you plan production?

You could worry about the other things that drive the bottom line. You could worry about labor rates or raw materials or transportation or energy or whatever it is. Water doesn't have to be one of them if you're a good water steward. Of course, there's cost savings and it's not just the water. Whenever you use water, there is at least a pump behind it, so there is energy savings. Often, there's chemical treatment savings. Before the water is used, you have to put some softeners or treatment or additives to clean it up to make it right for your use. There may be also regulatory costs associated with it as well.

Improve public image and help your _____ program are two other benefits. There are challenges, of course. Most notably, what we've noticed, there's not a whole lot of information from manufacturers to leverage. There's not a lot of tools, resources, or guidebooks or even experts out there which you could call upon as compared to the energy world. If you're looking for energy efficiency help, of course, as Bruce mentioned, as we're here today. Better Plants and the Department of Energy are looking to improve the situation with webinars like today and a guidebook that we'll talk about a little bit later and initiatives that we'll talk about too. Next slide, please?

So, the initiative, the Better Buildings, Better Plants Water Savings Initiative, which Bruce highlighted earlier, currently we're at 38 partners, as Bruce mentioned. Nine from the industrial sector. We listed them out here. Cummins, Ford, GM, Harbec, Nissan, Syncovane, Toyota, UTC, and BD. As you can see, not only are these guys early adopters of this water savings initiative, but they've also realized from really significant savings, over 40 percent for several of them. Next slide, please.

So, throughout this slide deck, we'll be highlighting some of the lessons learned we've been able to gather from our partners. Seven of the initial partners are pilot partners. Those would be Cummins, General Motors, Ford, Syncovane, UTC, Harbec, and Nissan provided valuable information to us surrounding barriers to water management and successful strategies and effective strategies for overcoming those challenges. The guidebook is available on the Department of Energy's website – or the white paper, I should say, at that link. The slides will be sent out after the recording so you'll have that link, and you can peruse that at your leisure.

The resource is divided into four sections making the business case for water, facilities and water sources to focus initial efforts establishing baselines and targets and water efficiency measures implemented. As I mentioned, we'll highlight many of the successful strategies used by partners throughout the balance of this slide, but if you really want to dive into these topics, I encourage you to visit the links. Next slide, please.

So, with that little bit of a background, I wanted to jump into a couple of technical areas to help you get started on your water management programs. One of the first thing is setting and tracking water intensity targets. Next slide, please. So, why do companies set targets? One interesting anecdote that I'll start off with is one of our water pilot companies mentioned that they had never implemented a water saving action until they set a target.

Targets are really motivational. I mean, I imagine with anywhere and anything we do, having that goal in mind that you can work towards and feel good when you accomplished it is a strong motivator. So, targets can really motivate that water management program at your facilities. Polling our partners, there's several other reasons. What I found interesting when we looked over the responses, what I would call the number one reason before setting a target, and that all the partners listed it, was environmental stewardship and corporate sustainability.

Companies are realizing, I think people are realizing, communities are realizing that water is very vital, very important, and it's becoming a more at-risk resource. So, I think we all try to do a little bit better, and then the companies reflected this. Also, the energy benefits from water reduction, and you'll see the risk there as well. We're also highlighted by more than half the partners.

I will point out that the overall cost of water pointed out as a driver for less than half of those that were responding. Not to say that there's not financial savings, but I think this is an interesting area where water is cheap. We hear of that a lot, and we hear people saying, "Much ado about nothing," and "Paybacks aren't working out." But there's several other reasons to be looking at water management and water efficiency, and there are cost savings too when you start looking at more holistic analysis. Next slide, please.

Developing targets. So, what type of targets? So, there's an acronym in the world out there called SMART Targets: specific, measurable, achievable, reasonable, timely targets. So, it's fairly straightforward, but you want to set a target that is achievable in the sense that you looked over your production, your situation, and the years coming forward, where you need to be with water and you set a target that has a specific metric behind it, so it's not vague. You put timelines around it, hold yourself accountable, and it's something within grasp, something you can do.

So, here we've listed our water pilot, our water savings initiative partners. As you can see – I'll pick on GM – they've set a specific percent reduction, 20 percent. They've given a metric of gallons per vehicle, and they've given you a timeline. They're going to start, and they've going to compare against 2010 water use, and they want to achieve this goal by 2020. So, it's very specific. It's a SMART target, and I'd say all of these are quote/unquote "SMART" targets.

Oftentimes though, the facilities themselves weren't the ones who were setting the target. So, for example, United Technologies adopted a corporate target. Cummins adopted a target that was handed down to them from corporate, and that target represented the U.S. due diligence towards the global target. Nissan got their target from the headquarters in Japan and said, "We can do better," and so they set something that they felt was more aggressive. Next slide.

So, back on that previous table, you can notice that there's a mix of targets. When we get into this, there's intensity targets. These are better for tracking water efficiency and efficiency in general. If you imagine you are doing great water efficiency work but your production doubles, you should be happy, but your water use maybe went up by – or your water use went up. That won't be reflected if you're doing something like an absolute target and just looking at the volume production of water. You'll still look like, "What gives?" You'll use more water.

Intensity metrics can start to correct for that factor and say, "Well, I used more water, but I was more productive with that water use." However, absolute metrics makes sense in some cases. If you're in an area where there just isn't a lot of water, frankly, the community, your water regulators, they're not really going to care how productive you are. They're going to know that there's this much volume of water in the lake, and we all got to share it. So, absolute targets can also make a lot of sense in the water space.

Some companies, many companies do both. So, you can set one target and one type of metric publicly, but you can track the other internally. As you see, Cummins, Ford, and Nissan do that. Next slide, please?

So, what I wanted to do is outline, walk you through how to track a water target. What I'll do here is we will walk through these steps. I'll kind of verbally describe them, and then I'll try to eliminate these with an example of a fictitious company and walk you through each of these six steps for how this fictitious company was able to calculate their change in water intensity. I want to note that while it looks like a linear approach here, particularly, your first time through, you may have to do a little bit of rinse and repeat. You might have to get some data together, fill in a spread sheet, graph it out, see what it looks like before you can get to your metric and before you can identify which variables and which factors you want to keep tracking.

So, but I think you can use this six-step approach as a guideline wherever you are in the process. So, the six steps are, step one, define your boundary. Step two, choose a baseline year. Step three, identify relevant variables, and we'll define what that is and/or the denominator for your water intensity. Step four is gather data on water use, and that variable from step three. Step five is to calculate water intensity, and step six is to calculate the change in water intensity. Next slide, please.

All right. So, define the boundary. What do we mean by boundary? So, that's the water sources and facilities whose water is being tracked. So, what's in, basically? When we talk about that 20 percent target, 20 percent of what? So, on the first one, water sources, we encourage to be more comprehensive and include all water entering your facility. This will create a stronger connection to other sustainability efforts and here what I mean is, again, get back to the idea that if you're using water, it's being driven by a pump in most situations, almost all situations. In which case if you're going to – that water does have an energy cost to it.

So, at a minimum, you should be tracking it from that perspective. It also is more reflective of the way water impacts our local environment in that if you're not including water that is self-supplied, that's taking water from others, potentially. So, we support including all water sources in your target. To walk through, what are some of the water sources? You have fresh and non-fresh, sometimes called saline.

So, freshwater sources include the one from your municipality. So, you want to purchase freshwater, so it's on your water bill. On-site surface or ground. So, surface water could be something that's on a lake, river, creek, stream, or reservoir that's on your plant, that your plant has access to. Ground is groundwater. Non-fresh could include seawater. I don't know how many people that's applicable to. I think, generally, in the United States, that not applicable to a whole lot of people unless you're on a coast.

Recycled and reclaimed water is interesting in that it's water from external source that's not suitable for potable. Maybe it's from your neighbor who is sending you over non-potable to use in your facility. That would be an example of non-fresh water, and then there's rain or storm water. So, if you're capturing rainwater, if you're capturing storm water off your roof and using it in your facility, you might want to track that as well. Next slide, please.

So, if you are tracking across multiple facilities, so if you're – yeah, if you have multiple facilities in your purview, we encourage you to set the target across all facilities. On one hand, as a positive to this, it encourages the sharing of best practices. So, you can take whatever one facility is doing that's great and share it amongst the other facilities.

Again, getting back to the idea of operational resiliency and growth and planning that all your facilities are operating as efficiently as possible will better prepare you for an unforeseen water issues. But as a caveat, we would say that only consider facilities in which you can actually affect change. So, facilities which you have direct financial operational control over. Next slide, please.

So, choosing a baseline year. So, this is going to be the year against which your improvement is measured. So, to pick on GM again, the baseline year of 2010. So, that means they're going to track that water intensity metric against 2010. They want to lose 20 percent against what they were doing in 2010. So, we encourage companies to select a baseline year that best represents your current operation. So, the one constant, I think, in manufacturing is change. What you were doing 5 years ago may not be what you're producing this year, and for the longer timeframes, that's almost certainly true.

As part of the DoE's programs, we strongly encourage companies to seek to establish a baseline of no more than three years prior to their current year. We use a little bit of flexibility in finding that baseline year, but it also helps to ensure that moving forward that baseline year stays representative of your operation. In selecting that baseline year, think about the data you have available. Do you have all the water data you need? Do you have all the relevant variable information you need? The baseline selection might also be something that's outside of your water efforts.

So, it might be aligning with broader sustainability efforts, that you could partner, for example, with DoE and the Better Plants Program. Perhaps it has some linkage there with our energy goals or something like that, or perhaps it's an internal corporate initiative. Finally, there's a baseline year. So, we're using the term year, but what we really mean is select a baseline that encompasses your full operating cycle in any – if it's 12 months or whatever it might be. Capture all the seasons, energy and water use.

Energy and water use, yeah, will change over those – are likely to be impacted by the seasonal conditions, and it might not just be weather. It might be the Christmas push or something like that, or maybe the summer lulls that you want to be able to capture in that full year. Next slide, please.

Step three is identify relevant variables or water intensity denominator. So, we're going to talk a little bit about different ways to track and ultimately, what we're trying to do here is you have your water use, but you want to understand what drives water use? You want to collect data on those things that drive water use. So, if you're a facility where you're using water for – let's say, you're a bottler or soft drink manufacturer. Water, of course, is going to be – your water use is going to be dominated by your production in that case. That's a very obvious example. Other examples could be where you're using a whole lot of steam in your process, if you're doing a lot of cooling in your process. If you're a food manufacturer, and you're doing a lot of rinsing and washing or textile manufacturer, if water is used heavily in production, then you will want to consider at least a metric that encompasses or describes your production output.

Water is used for domestic purposes, meaning you have showers and restrooms and a lot of employees. Maybe it's less automated and more human sort of work. The number of employees and the number of shifts or some sort of indicator of how many hours are being worked may be what drives your water use, and may be something that's good to keep tabs on to try to understand what would be a good metric for water.

Water is another metric. So, if your facility is cooled with an air conditioning system that's based off of a chilled water system that has a water cooler or that uses water cooling, well, the that's going to be – weather there is going to be a factor in your water use. Or if you raw material is sitting outside, and it rains, it gets wet or it's cold or anything like that. That might impact your water use as well and your energy use. So, you might want to consider one of those cases. Keep in mind that it's likely that's not one variable that drives water use.

So, there's a couple of methods that we'll talk about how to track water intensity, and one of those methods you can use more than one variable, and one method you use a single variable, more or less. But keep in mind that it's not always one variable that's driving water use. In fact, it's probably more than one variable, and you may need to just try some things out, see what works your first time through. Next slide, please.

So, gather water use and relevant variable data. So, go back now that you've set your boundaries; you've defined your baseline. You have identified what you think is affecting or causing you to use water. Now you need to start going back and gathering data. So gather data from starting at that baseline year and for each successive year. We'll walk through an example on those to kind of illuminate it a little bit better. A couple of points; as you're gathering data, make sure that it's tracked at the same frequency. So, for example, if you're gathering production data and water data, and your production data is coming in monthly, make sure you collect your water data at a monthly. We recommend monthly as a good frequency. So, 12 data points in any given year.

This means you may need to think about, "Well, my water bill comes in quarterly. What do I do?" or "My water bill comes in every – some odd number of days. What do I do?" You may need to just apportion out if it's quarterly, divide it by three to figure out how much water is used each month, and then do some estimation techniques to get to monthly or to make the frequency the same.

Finally, we recommend using some sort of spreadsheet or electronic device to store your data. This really allows for easily to update it. This allows for legibility. You could share it, and of course, you can fully leverage the power of just graphing the data or just looking at the data and better understanding and then playing around with the numbers if you're tracking it in a spreadsheet. So, a common place others can access to where you're storing your data really can enable this whole process. Next slide, please.

Where to get data? So, yeah, where to get data. So, to determine water, there is direct measurement that's off of your water bills or it could be on-site meters if you're doing self-supply, and it's not billed. There's estimates that you can go off your pump specs or equipment specs, and we're going to talk a little bit about that later on. Relevant variable information, you can gather production data from a variety of places. We listed a few there. Maybe you're talking to your financial department who is keeping tabs of orders or something like that. Maybe looking at production log sheets. Maybe looking at inventory. That's one way to get production.

Weather data; we've listed a NOAA website that can give you good weather data to help you with this. Next slide, please.

Step five is going to be calculate your water intensity. So, we have defined the boundary. We have selected baseline year. We've thought a little bit about what drives my water use. We've gathered some data on water use and what drives my water use, but now it's time to calculate your water intensity. You have a couple of options here. So, water intensity approaches on the left side. So, this is essentially a ratio. Most of our partners you saw there were using water intensity, as we talked about. So, gallons per vehicle or gallons per unit of something, some physical output.

This accounts for any changes in water use associated with any changes in production. So, as we talked about, if you're getting more efficient, but your production is doubling, you might not capture unless you're using an approach such as the water intensity approach. However, you may need to create something called a standard unit. So, if you're making seven different products, and they all vary a little bit – maybe it's seven different chemicals with different water uses or something like that – you may need to create a standard unit that says, "Well, here is one representative unit of product that represents all seven of my chemicals." Maybe now your standard unit is based on volume of chemicals, and there's methods where you could take that volume of chemicals and say, "Well, this one requires this much water, and this one requires this much water per pound," and kind of come up with an aggregate standard unit.

We have some resources to help with that. On the right-hand side there, there is a hyperlink I'll talk a little bit about and then we can – it has a little bit more information on how to do something like creating standard units. When you use the water intensity approach, you're going to calculate a change in the next step, and that's based on the change in this metric. So, it's an improvement in productivity.

Now, what we call the more advanced approach is the one on the right-hand side. It's a regression-based approach. It's what we recommend on the energy side of our program where we really encourage our partners, and the TAMs are there to help to get started or to track energy using this regression-based approach. For water, we still really would encourage partners to try and go at it. However, it's not easy for partners right now with water, and we're still working out some of the finer mechanisms of how this might work out, but we really think it could be a valuable way to track water. So, what is it?

So, it uses statistical modeling to estimate water use, and then compare that estimate of water use to what you actually did, how much water you actually used. I think the couple of really big benefits that I see is that in regression-based approaches, it really isolates your water efficiency improvements. So, your model is going to look like something like – well, let me get back. The second thing that I really like about the regression-based approach is where the water intensity approach only really allows you to look at one metric; regression-based approach lets you look at a few metrics that will drive water use.

So, for example, so you might have your baseline here. What you'll do is you'll collect your data. You'll collect those variables that you think impact it, and you can use tools like Department of Energy has an Energy Performance Indicator tool that's for energy, but really, it's just a statistical tool, and you can use it for water too if you just kind of put your hand over energy and call it water; it should work. But the idea is that you create an equation that describes how your water is used. So, water equals and then an equation that has all of those independent variables in it.

So, when your production goes up and weather goes down, you can kind of account for all of these changes because you have a model. You'll take that model; you'll populate it with data from your current year, and it'll tell you how much water you should have been using. But now you're using less water than what you thought you were going to use because you're so efficient and you implement all these measures. The regression-based approach looks at, "Well, had I don't nothing, I would have used this much water, but I've been doing all these great improvement projects, and I'm using less water." The regression-based approach can really capture that.

So, for more guidance on this and the water intensity approach, I encourage you to go to that hyperlink. It's for energy, but I think that the principles really do apply for water. Now, for this slide, these slides, recognizing the regression-based approach is a little bit more rigorous, we're going to focus on the water intensity approach. Next slide, please.

So, once you've selected your method and you've calculated your intensity, now you're going to calculate your change in water intensity. This is pretty straightforward. Look at the value, whatever it was and your baseline year. It's your current year if you're using the water intensity approach. You're just comparing that ratio in the regression-based approach. You're comparing your models versus your actual use.

I should say that regression-based approach, there are a couple of different ways in which you model. There's forecasting and back casting. We don't need to worry about that, but generally speaking, it's looking at what you are estimated to use and what you're actually using. That's going to be your percent change. Improving in the water intensity approach represents and improvement in productivity of your water use, and regression-based approach represents avoided water use.

I think if you can go to the next slide, Bruce, I think we'll pause. I'm going to get to an example of each of these steps. I'm sure it was kind of quick, but hopefully, the example will help. But I want to pause and see if there are any questions.

Bruce Lung:	Thanks, Prakash. Yeah, at this time, please let us know if there's any questions. Ray, if you want to take people off mute? Does anyone have any questions for Prakash on the last set of slides? I think we've covered a lot of important information there, particularly, the SMART Framework. That's what we use through our partners that want help with their water efficiency and tracking and all that. If everything seems to be making sense, then we'll go ahead and continue.

We do have a fair amount of slides, but I wanted to stop and make sure everyone had a chance, if you had any questions, to ask now. Okay, well, what I'll do is we'll just keep going through the next section, and we'll pause it in a little while to see if anyone has any questions at that time.

- Prakash Rao:	Sounds good.

Bruce Lung:	So, if you want to go ahead, Prakash. Thanks.

- Prakash Rao:	Sure thing. So, I want to walk through an example. Next slide, please. So, here is a fictitious plant, Smith Stampers. It's committed to the city-wide goal to reduce their water intensity by 20 percent by 2020. They're now beginning to say, "All right, what did we just get into? How do we track progress here?" Next slide, please.

- So, we're going to walk through that six-step approach. So, they defined their boundaries, step one. Smith buys water from the city, and they are pulling water from the ground. They have two water uses. They don't really know how much water they pull from the ground. No one has really asked them. No one's really cared. But they recognize that the water they pull from the aquafer or the ground is less water for the next person over. So, they want to include that to show environmental stewardship.

- So, say, our boundary is going to include both. They're a single facility, so the boundary also includes their facility, of course. Then they need to select a baseline year. Let's just imagine here at Smith that many facilities that have made a change to one of the production lines where it completely was swapped out in 2015. It's 2016 this year – or 2017. Anything 2015 and before really doesn't represent their operations. Other things that could have happened; maybe there was a change in management in 2015. Maybe there was new equipment coming online, major equipment coming online that could have impacted water use.

- You're tuning this thing up in 2015 and the water is kind of using a lot of water at times. Maybe there was major construction. Again, think about your current situation. So, Smith thinks, "Well, 2016 is my current situation." So, they're going to select that as their baseline year. They have the data, and they think that's what's going to represent them moving forward. Next slide, please. So, they got their baseline year. They've got their boundary. They're now going to think about relevant variables.

- So, facility management gets together. They start to think about what drives water use. So, they have a lot of rinsing parts. They have a lot of water cooling. So, they know production is driving it. They want to track production. I'll say they're a two-shift schedule, 100-something employees. Water that those employees, of course, are going to be using water. They're coming in. They're drinking water. They have showers. They have restrooms, and they don't really know. They think it's a small water use. It's a manufacturing facility. It's generally more for the commercial side, but at the first path, let's track that, see how it compares to production.

- Finally, they use their air conditioning, and they use a cooling tower. So, they know that their water use goes up in the summer, or they think that the water use should go up in the summer based on this. So they say, "All right, well, let's include some measure of cooling degree days." So, they include all three. Next slide, please.

- Next step is to gather data on water use. So, they grab their bills from 2016. They see that things are reported quarterly. They divide it by three for each month. Let's say, they're doing January through December – that's their 2016, so it's calendar year – and they're able to get that. That's pretty straightforward. What's less straightforward is that water they're pulling from the ground. Again, they have no meter or anything like that on it, so they're going to have to estimate it.

- There's three options we'll talk a little bit about. You can do field measurement. You can estimate this based on what's called "pressure head" or you can estimate it based on the power consumption. So, pressure head, just to review, is essentially the pressure to which the pump has to operate to overcome all the losses in the system and deliver water at the pressure that you need at the end use. That's pressure head. Each technique has its pros and cons. So, if you're go to the next slide?

- The field measurement; there's a couple of ways you can do it. You can do non-invasive, non-contact, like an ultrasonic flow meter. Pros here is where the other pressure had and power consumption are going to require pump curves, this one doesn't. Many plants don't have their pump curves. These pumps are age old. So, getting back and trying to find the pump curve is not a doable thing. Another pro; it's a direct measurement. So, it's less of an estimate.

- However, the non-invasive features or methods need to go get an ultrasonic flow meter. Those could be a few thousand dollars, and their readings may not be accurate if the meter is not installed correctly. So, you've really got to know what you're doing, or you can kind of get a lot of different flow rates that aren't representative of your situation.

- There's in-line field measurements. So, there's one-time set up. Pros of those is one-time setup. So, this could be something like a turbine meter that would go into your pipe and measure flow. It doesn't require pump curve, but as you can imagine, it requires stopping a lot of flow, cutting open your pipes, sticking one of these meters in. So, it's fairly intrusive. It's very intrusive, and they require some work there to install. Not as easy as the non-invasive methods.

- Those are the direct measurements, but there's a couple other things you could do if you do have your pump curve. So, you can look at the pressure head and the power consumption. We'll talk about how to do that in a little bit. They're pretty straightforward, but I think the big detraction on both of those is they require a pump curve. The pressure head one also requires some – it does require measurement of the pressure across your pump. If you don't have that, you might be stuck.

- The power consumption method, those require estimate of power consumption – or measuring power consumption of your pump system, but more importantly, there are some cons in that you have to make some assumptions around system efficiency, operating on a load factor, power factor. That really could impact your estimate of the water use. So, next slide, please.

We'll talk a little bit about an ultrasonic flow meter. For those who are not familiar, these are pretty neat. They use the Doppler effect, which is the same thing on our weather maps that we watch on the news. So, the idea is that you have a transmitter and a receiver. You put it around your pipe. The transmitter sends out a pulse to the water. So, the water, even potable water has a bunch of little things in it that are safe to drink, but they're in there. It's not pure H2O.

The ultrasonic flow meter will send signals out that will reflect off of those little things in the water, bounce back to the receiver. They bounce back at a different, what's called frequency and wavelength, and that's going to the difference between what the ultrasonic flow meter sent and what it received. It can calculate a flow, a feet-per-second or something like that. You multiply it by your cross-sectional area, and there you've got a flow rate.

The challenge here is where that particle is in the pipe is going to impact the velocity measurement. So, if you're tracking a particle right at the wall, those particles, just based on physics, move slower than the particles in the center. So, if it's a turbulent flow, I think that can also impact things. So, it has its caveats. Next slide, please.

Now, if you want to use one of the pump curve methods, there's two that we talk about here. There's one so you can use the head method. So, I have a pump curve I pulled off from the lab. What you want to do is measure the difference in pressure at the inlet and the suction end of your pump and that's going to be in something like PSI, pounds per square inch. Multiply it by some factor to reflect what's on your pump curve. So, in this pump curve, feet is on the left-hand side, and you're going to use that total head to estimate your water use.

So, here on this pump curve, as you see, there's a lot of lines. So, maybe I should start off with talking about what lines we have here. So, on the X axis, on the bottom you have the flow rate. So 0 to 1400 for this pump. On the Y axis going up, you have the total dynamic head, that's 0 to 550. You have what you're seeing is four sloped curves coming down, and those measure the different pump impeller sizes. So, 10.88 down to 8.88. The little curvy lines there are the efficiency points. So, if you're operating at a flow and a pressure on a given impeller size for your pump, you can figure out what the efficiency is there.

The last thing is on the bottom, this is actually showing two pieces of information. It's also showing the flow rate associated with the brake horsepower of that particular pump. So, the brake horsepower is the amount of power, fluid power that the pump is developing. So, in this case, if we're using the pressure head method, let's say that the folks at Smith's know this is their curve.

Let's say they have the 10.88 diameter impellers. Let's say they figure out that their flow rate is – or sorry – their head is across the pump is 450 feet. So, if you follow 450 feet on the horizontal across to the 10.88, I think I said, you'll see that the flow rate is about 1,000 GPM. So, that's one way to measure the flow rate. Now, let's say you don't have a pressure measurement across your pump; another way to do this is you get your CTs out, and you can measure the electric draw by the pump system. Measure the current and the volts at the pump system, maybe at the control panel. Use the equation down there to estimate what's the brake horsepower.

The two things that you see there, the V is the volt, the I is the currents. You got that from your measurement. Spur 3 is spur 3. Thousand is the conversion factor. But the power factor and the system efficiency; the power factor is something that some of these CTs, some of these power loggers, you can measure that, but if you can't, it's something you have to estimate. One place you might want to look is your energy bill. Your electric bills might show you what your facility power factor is. It's not necessarily what your single equipment power factor is, but it gives you a ballpark. You're also going to have to estimate your system efficiency.

So, what you're measuring is you're measuring the energy going into the pump system. Remember brake horsepower is the energy coming out of the system. The difference in that is called the system efficiency. So, you're going to have to come up with some measure of what the system efficiency is. I'm going to highlight a couple of DoE resources moving forward on pump systems that can really help you figure out system efficiency. There's tools available, guidebooks that can give you some rules of thumb, some estimates based on your pump system to figure out what the efficiency might be.

So, I'll say in this case, it's a 10.88 diameter impeller. Let's say they measured the current volts, and they found the brake horsepower to be 100. On the bottom curve there, you look at the 100 on the right-hand side. You follow it along to the left until it intersects the 10.88 diameter impeller pump, and you have about 600, maybe a little bit over. Oh yeah, about 600 GPM. Next slide, please.

All right. So there's some ideas of how to measure the water use so they get municipal from the bills. Groundwater, they measure, they pick one of those methods. Sum that up. As you can see here, they're gathering the data. It's an Excel-based spreadsheet. You don't have to use Excel. Whatever spreadsheet you want to use, but at least it's electronically stored. You can compute numbers on it. January 2017, you can just add right to it. You can share this. In addition to water use, it also has the relevant variable data. They got CDD from NOAA. They got labor hours from their shift schedules, and production from their logs. Next slide, please.

So, they take those three metrics, and they don't really know which one to go with. So, I would encourage initially when you're going through this, just plot them out. See what they look like. So, here, what we're looking at are all three of those metrics. So, the one I want to look at is water and each of the metrics. I want to see, look for trends. Where I see better trends, I'm thinking that's a pretty good metric. This is kind of loosely scientific, but it works, I think, after the first order.

Look at the top left. Okay, so CDD is in green there. That's the Cooling Degree Days. That's the measure of how much cooling is required for the facility based on the outdoor temperature. It spikes in the summer. Water use doesn't. Water use is pretty flat. What I would say is throw that out. It commonly finds the intensity metrics, CDD and HDD aren't really denominators, but are used, and in this case, that's bearing true. So, we throw that one out.

Come to the top right. You have 1,000 gallons. Again, on the left-hand side, we've got labor hours. We were thinking, "All right, there's a lot of employees here. Maybe they're impacting our water use." You'll see the shift schedules, the number of operating hours. They're going up and down, but again, the water use is kind of staying the same. So, labor hours maybe isn't the best metric. Now, on the bottom right, we're looking at production. That's the number of units they shipped out the door, and the left-hand side is thousands of gallons again.

But you'll see in the green that production is going up. Blue, water use, is going up. Put a little line, a trim line on the water use because it's kind of fluctuating. It's not only dependent on production, but it's dependent on some other things. It looks like the first order of production and water use are tracking together. So, we plot that out. You can see a lot more when you just visualize your data. So, you get your data on your spreadsheet. It just looks like a bunch of numbers. When you plot it out, you could just really see a lot more trends and understand what your – get some better ideas of how these numbers relate to each other.

So, in this case, Smith says, "Let's go with production as our water intensity metric." I want to point out that if you did a regression-based approach, that perhaps it is production and labor hours that are really driving water use. Maybe in the summer, CDD is actually impacting a little bit, but other factors, you really can't tease it out just by looking at something simply. So, maybe CDD really is driving water use, but really the employees are using water differently or something like that so you're not really able to see that effect. It's getting muddled. Regression-based approach can really pull these things out, but again, it's a little bit more challenging to take on. Next slide, please.

So, they've defined their boundary, selected a baseline year. They went through and got a bunch of relevant variables. They gathered data, and they figured a relevant variable that they like. They got water intensity metric that they like. Now they're going to calculate it. But here, we're back to our spreadsheet without the 2016 water data. Essentially, what they're going to do and what we do for the Better Plants program is we track this stuff annually. So, we're going to total the water use, total the production for the 12 months of 2016 and just divide the two. So, the water intensity there is 0.23.

Now, as you can see, you could track it monthly as well if you want to do a little bit more granular tracking to see how water intensity is moving. That could be a really important what is called performance indicator. So, let's say your water use spikes through the roof one month. That should raise an alarm to say, "Hey, what's going on? Why is our water use –" and maybe it's totally expected because you have so much more production. Maybe it's not.

That cold really be something like a big indicator of a leak. That can be how you can identify your improvement opportunities. So, it's a great metric, something to track on an ongoing basis. The spreadsheet will help you do it. You can calculate the water intensity metric on a monthly basis, an annual basis. For our purposes here, we're looking at tracking water metrics, and the next step will be calculating change and annual improvement. But that's not the only way you can use it. You can use it to identify outliers in water use or identify issues.

The issue might not even be – water might be your smallest issue. Maybe your water use is spiking and that's a problem, but it could be pointing to a much larger issue that you'll need to address. By tracking water use, you're able to get ahead of that. Next slide, please.

So, calculating your change in water intensity, that's the next step. So, Smith is in this city-wide program, the one that tells folks how well they did towards meeting that 20 percent target. So, they had the water intensity in 2016. They keep adding to that spreadsheet. They got the 2017/2018 water intensity. There's a couple of different ways to do this. So, you can look at your total improvement in 2017. That's just going back to your baseline year.

So, you're looking at the water intensity in '16 minus the water intensity in '17 over the water intensity in '16. That gives you about 4 percent there, 4.3. Do that again for 2018. That give you improvement over 2 years. 7For Better Plants Program, we say subtract those two. So, the difference between the '17, the 4.3 and 13 percent represents your improvement in 2018 against that 2016 baseline. If you're moving your baseline, let's say you're tracking it every single year, and you want to re-baseline every year, which is certainly an understandable thing to do. Companies do it.

In fact, utilities maybe encourage it if you're partnering with them. You can kind of just follow along how you calculated your total improvement to get your annual improvement. That's that 9.1 percent there. Next slide, please. I think we're going to pause here again. We have a couple more modules I wanted to go through, but I do want to pause for questions. As we move forward, we're going to move away from tracking water intensity and setting targets and getting to some water efficiency measures and just talking a little bit about system water use.

Bruce Lung:	Thanks, Prakash. I also want to make sure, in the interest of time, that we're addressing everything we need to here. It's 1:34 on my clock, and so I just wanted to check in and see if anyone has any questions right now. I know we just covered a lot of technical material. So, please don't feel shy and let us know if you have anything on your mind.

Alissa:	Hi, this is Alissa from Honda.

Bruce Lung:	Hi, Alissa,

Alissa:	Hi. All right, so yes, lots of technical information was just shared. Is there any way – so, I'm, of course – that's why I'm listening to this. I'm not an expert.

[Crosstalk]

Someone else needs to mute.

Bruce Lung:	Yeah.

Alissa:	Is there a way or would Better Plants be able to help in some of this technical information as far as collecting that baseline along with the supply base?

Bruce Lung:	So, I think I'll take a quick shot at that and, Prakash, feel free to jump in. I think the answer is yes in the sense that for our partners that are interested in drilling down on their water intensity, your TAM will be able to help you with all of these equations and analyzing the data in this way. So, I think, for example, Wade would do that with Honda, and he would also do that with suppliers that are in Better Plants of Honda that are in that supply chain cohort.

I think where we have a little bit of difficulty is if it's a supplier that's not really in the program. We might be able to give them a half hour or something once in a while, but I think we'd really want them to be in the program in order to get – because it would require a fair amount of time to be able to do that.

Alissa:	Understand, understand. Does anyone else have a question? Because if not, I have one more.

- Bruce Lung:	Have at it.

Alissa:	All right. So, the – oh, I just lost my train of thought, Bruce. [Laughs] Story of my life. Story of my life.

- Bruce Lung:	Well, let me do this.

Alissa:	Okay. I'll think of it.

- Bruce Lung:	Let me do this while you're still thinking of it. Let me just open up and ask how helpful has this information been so far to the folks on the phone? Is this something you think you can use right away? Are you interested in learning more, that kind of thing? Please give us a quick yes or no or whatever you think.

Male:	I think that – [break in audio]

- Male:	Useful.

- Female:	[break in audio]

- Bruce Long:	It sounds like there's some background noise. Somebody may want to mute their phone if they've got people in their work station or something. Alissa, I don't know if you still –

Alissa:	I thought of it.

- Bruce Lung:	Okay, go ahead.

Alissa:	I thought of it. Okay, so at the beginning you had mentioned possibly a Nissan or a GM. As an OEM, how have they set their targets? This is very new for Honda North America, and we're not setting any requirements at this point, but Lisa and I are trying to put together what is, I guess, acceptable or realistic for our supply base?

- Bruce Lung:	Okay. I don't know, Prakash, can you handle that?

- Prakash Rao:	Yeah, so just to confirm, Alissa, you're talking about setting targets for your suppliers, not for Honda itself?

Alissa:	Well, it would be a Honda North American goal that we would ask suppliers to help achieve.

- Prakash Rao:	Sure. So, in the cases that you mentioned, Nissan and – at least Nissan, they had the corporate handed down to them by – sorry. They had their target handed down to them by corporate. I'll highlight on one company that we weren't really mentioning, is UTC. So, they have, if you go to the Better Buildings Solutions Center, they have an implementation model, and it describes how they set their water management efforts for each of their facilities globally. What they do is they start with a tool called – they're really focused on scarcity issues. So, they use a tool called World Business Council for Sustainable Development's Global Water Tool.

- It's got a little bit of information on it on the backend here where it says, "How much water do you use, and what's your risk?" If you really are a risky location, they have a list of water measures you have to implement, and that will – you'll have to do all ten of them, for example. But if you're not a risky situation, you may only have to do two of them. That really prioritizes the efforts for UTC. I heard a hello. Can people hear me?

- Bruce Lung:			Yeah, we can hear you.

Prakash Rao:	Okay.

- Alissa:	You're doing great.

Prakash Rao:	Okay. So, that prioritizes efforts. As far as targets themselves, I think it's a combination of factors of not only what is the local situation with water, how much has the company done in the pat? Is this company or the supplier or whoever it is, really been at the forefront of water and really been pushing it, and there's really not a lot left? Other ways, other things to think about are broadly, if you know you're not doing water balances or leak checks in your facilities, you can probably guess there's a lot of opportunity on the floor, right? So, you might be able to set a higher target because you're still picking that low-hanging fruit.

But I think it's very situation-specific and just kind of thinking of, "Well, based on our historic water conservation efforts, where do we think we are?" Looking across to on the energy side, you can look across the benchmarking and say, "Well, what are other people doing?" Water is a little bit tougher to do that, but if you do have the opportunity to sort of share information [phone ringing] where different folks are, that might help you as well set the target.

- Bruce Lung:	Yeah. One other quick thing I'll mention, and then we'll keep going is for the water efficiency initiative that our partners participate in, the minimum that we ask them to commit to is 20 percent over 10 years. So, that just kind of gives you an idea of what we think is kind of the industry potential over a 10-year period.

Alissa:	That helps greatly. Thank you both so much.

- Bruce Lung:	Sure. So, we'll keep going here, and go ahead, Prakash.

Prakash Rao:	Sure. So, I want to – I'll move a little bit faster. I wanted to go a little slow in our previous part, but I will move a little bit faster here. So, I want to talk a little bit about – so, you're tracking this water intensity metric. You're doing great, but how do you do those projects, right? That's what's going to get you water savings, not just tracking stuff. So, Cummins, Syncovane, and UTC all said the first thing you got to do is develop a water balance. How much water is coming in? Where is it used? How much water is going out?

From this, you really find leaks. Leaks are a huge source of water savings. A 1-GPM, one gallon-per-minute leak is over 500,000 gallons per year. So, that could be something you pass every day, but if you fix it, that's 500,000 gallons. This also is demonstrating novel approaches that DoE is featuring on their website. Next slide, please.

So, here is a picture of a water balance from Cummins. So, on the left-hand side you have water coming in that's public and on-site well. The right-hand side in the green bubbles you have water leaving. In the middle in the blue, you've got water by equipment use. We talked a little bit about how to do – doing a facility water balance is not something you can do in your sleep. It takes some work. But we talked a little bit about water coming in, how can you get that balance? Then we talked a little bit about the equipment, how can you look at that water use?

On the disposal end, that's something you can get from your bills for if it's going to sanitary/sewer. If there's a pump behind it; we talked a little bit about pump estimation techniques. So, there's a couple of ways you can estimate that to help develop your water balance. We'll talk a little bit about that. We talked before and we talked afterwards. Next slide, please.

So, data collection for conducting a balance. What we observed is meter for billed sources, combination of estimation techniques for other sources. The one I want to highlight is the estimation techniques. We presented some pretty technical ways that we think are more accurate. There are other ways you could do it just based off of, "Well, I know my equipment are supposed to use this much water. So, this is how much they used per year."

The one thing we learned is an estimate is better than no estimate. So, even if it's a lag, that's better than not knowing. As you can see here, most of the water use is tracked at the facility level. The partners did have a challenge. They knew where they used water within the plant, but they weren't always able to track it. So, if you're looking at this and you're saying, "Well, gosh, I don't know how much my equipment uses. That's a difficult thing," you're not alone. [Laughs] So, we're trying to promote advanced best practices here, and that's part of it. Next slide, please.

So, the next two slides – the first one is Harbec, and Bruce if you'll go to the next slide, Nissan – these are two really great examples of water saving projects. Harbec has a really innovative project that were using rainwater. Nissan is a really great project of treating water and recycling the water to realize substantial savings. Both of these examples are featured on the DoE's Better Buildings Solutions Center. Bruce provided the link before, and they'll be in the slide deck, and you can capture the Nissan or the Harbec page, and you can really capture the details there. But in the interest of time, we'll have to go to the next slide.

We asked our pilot partners to say, "What did you do? You got these 40 percent reductions. Can you just give us an idea of what sort of measures you're putting in place?" Number one, again, is leaks. Leaks, leaks, leaks. [Laughs] The other things were broadly _____ and monitoring controls, recycling, and reuse. The other page is – the next slide you'll see training and water storage and substituting water. In general, some of the big things: leaks, closing open-loop systems. So, that's like using a cooling tower, which we're going to talk about in a little bit. Training your operators, operating equipment closer to spec.

All the partners said one thing; if you're doing the project just for saving water, it's probably not going to pay off unless it's something like a leak repair or something simple. One thing they all mentioned is when you're dealing with an energy project, think about the water savings behind it, and that's how you can start to tack on water savings. Water might not be what's blowing down the bill or gaining that capital financing. That means companies like capital financing for water projects are _____ dedicated pool.

But if you're thinking about water when you're doing the other facility improvements, then that's the way you can really realize substantial savings. Next slide, please. So, maybe we won't pause or we could pause for a minute maybe to see if there's any questions on that. I know I kind of went through it quickly. What's coming forward is a couple of deep dives into pumping, cooling tower systems, and if we have time, steam systems. [phone ringing] But I want to pause to see if we have any questions on those measures.

Bruce Lung:	Anything right offhand?

Male:	Just two thing I got. One is we have some remediation systems that some plants may have ongoing where they're pumping water and then reinjecting or treating and send it back into the environment. You wouldn't be looking at those in this particular program, would you? That's one thing. Usually, those are out of our water type systems because they're never really involved with your plant operations.

Then number two would be there's a lot of plants that have already done a lot of things with cooling towers and different things like that. So, when you get into doing some of the water reduction efforts, how are you guys looking at 20 percent from somebody who feels they've done a lot with their systems?

Prakash Rao:	Yeah, sure.

- Male:	Those are just two.

Prakash Rao:	Bruce, if you want, I can start and then you can jump in.

- Bruce Lung:	Yeah, go ahead.

Prakash Rao:	Yeah, sure. So, I'm going to start with the second one. I mentioned when you set your baseline here to set something that captures the current situation. But you can also bring it back a little bit to say, "Yeah, you know what? I just did this huge capital investment last year, and I really want to capture that because it was a big project for us." So, maybe when you select your baseline, you're capturing that new cooling tower that you put in place and that's really saving a lot of water, closing some open loop. So, that's one way to think about that.

Then the first question, I think, if I understand it correctly is if you're using water, and then you're treating it, and then disposing it back to the ground, does that get counted as water savings? Is that right?

- Male:	Well, it's a little bit more of remediation systems. So, you're going under US EPA or one of the big agencies, and you have groundwater contamination. You're running that through some sort of treatment system, and then cleaning it up, and then you're putting the groundwater back into the system. That's really – that's sort of a balance right there. I mean, it doesn't particularly have anything to do with manufacturing and everything. So that's not really involved in this as far as what you guys thinking is.

Prakash Rao:	It could be though, right? So, if you're thinking about – if I understand the situation correctly, I mean, you're saying right now the water doesn't really enter your facility, but a great opportunity now is you've just taken water; you've treated it. I think one of the biggest things that we should think about with manufacturers is when walking around, ask yourself, "Do I need potable water for all this stuff that I'm doing right now?" I think the answer is usually no. In fact, in the case of Harbec, their goal is to be water neutral. They said, "I don't need potable water for anything. I just need it to drink and wash my hands." Their water neutral goal is to replace potable water use with rainwater for everything else that's non-domestic use.

So, if you're pulling water from the ground, you're treating it, and just sending it back to the ground, one idea is, well, why don't you use that in your facility? That might now bring down your water use.

- Bruce Lung:	All right. So, does that answer your question?

Male:	It's a good answer. I'm actually using it for energy recovery, but that's another way, yeah.

Prakash Rao:	Sure. So, I wanted to highlight a couple of systems. First, let's start with pumping. As we said, saving water saves energy. You might not always be saving all the energy you could. So, at a first approximation, the energy required that your pump is producing is proportional to the cube of the flow. It's called the affinity laws, which is based on physics. It's really a theoretical thing. Usually, it's not exactly to the third power or something smaller.

The idea is that you could be – when you reduce your flow rate, you could be saving a lot of water. If you're reducing your flow rate by half, your energy consumption might be an eighth. That's the only thing what you require, but if you're not making adjustments to your system, you're not going to realize that savings. If you go to the next slide – so, here we have a pump curve again. The original operating point, the folks are operating at 1,200 GPM. Let's say they do some great measures and they drop down to 1,000 GPM, and they didn't do anything to their pumps. They just kind of the same pump system. They didn't modulate there.

They're going to ride up that top curve, which is the pump curve, and they're still going to save energy probably because energy is going to be flow times head, so they're using less energy than they did before. But what they're probably going to do is operate at the top X and then drop with the throttle down to the bottom X. All that throttling is pressure energy that you just delivered all this pressure to your system. You throttled it down and just blew it off. It's energy loss.

You could do a couple of things. If you know that you're always going to be at 1,000 GPM, that's where you are now; it not going to go back up to 1,200, to you it's called impeller trimming. You can trim down your impellers. You can create a new pump curve, which is the little curve on the 1550, 1350 curves. You can operate along the system curve, and you can operate at that bottom X; or you can install variable frequency drive, in which case you will back off on the pump speed, and you'll be able to ride the system curve and operate at that lower operating point.

So, in both cases, adjustments to pump systems offset the throttling energy losses. You're able to realize the full savings, energy savings from your water savings. Can you go to the next slide, please?

So, we talked a little bit about this. One thing to remember with impeller trimming for substantial reductions in water use, it might not work out; you might just need a new pump. With variable frequency drives, we often see people just think it's the answer to all problems. It really isn't. You really got to look at your pump curve. Make sure you don't have really high static head; otherwise, you're not going to see savings. Make sure when you do your calculation economics, you recognize that there's losses across the VFD and the motor, and those grow substantially when you're operating at lower load factors, make sure to include that in your calculations. Next slide, please.

The Department of Energy historically has put together a whole host of resources on the system and particularly in the Advanced Manufacturing Office on system energy opportunities. Pump system resources from DoE are available at that link. There's software tools, a pumping system assessment tool, and that's currently being updated by Tom and the folks at Oakridge to make that even better.

There's literature out there, the sourcebook, tip sheets, case studies on pumping efficiency measures and how to implement them and where to get help. There's even training. There's a list of experts who can come into your plant and help you out. There's online training as well.

[Crosstalk]

Bruce Lung:	Cooling towers. Yeah, one thing I should say. We spoke to the folks at GoToMeeting, and we got an extra 10 to 15 minutes for this call. So, if anyone has any questions right now, feel free to submit them; otherwise, we'll just keep going.

Prakash Rao:	Sounds good. The cooling towers, I want to focus a little bit here too. Next slide, please. So, cooling towers are really a great way to get out of once-through cooling – which uses a lot of water – start to recycle water, and save significantly on your water bill. I will point out though that what you're really doing is trading off water use for water consumption. If you get back to that term that I introduced earlier. So, the cooling towers evaporate water for cooling, and that sends it out of your watershed. So, the water use is a little more environmentally impactful, but overall, it's a lot less.

It's a very common equipment. We often find that cooling towers are not always in the best repair, or if they're operated on feel. So, there can often be a lot of opportunities on these forgotten systems. Next slide, please. So, the principles of operation, I just want to cover really quickly for those not familiar. In this on the right you have some sort of refrigerant cycle, and it's cooled by a condenser. So, the condenser has heat. You use water to transfer the heat, take it away from the condenser. It goes to a cooling tower, comes in the top of the cooling tower, and trickles down what's called fill.

I'm showing what's called a crossflow tower here. As this water trickles down, air is pulled through with a fan at the top across the water in a perpendicular direction, a countercurrent perpendicular. Where the water and the air meet, there's evaporation taking place and that cools the water down. The basin or the sump, you get cold water, which then goes back to your condenser and that does the cooling. Out of the top of your cooling tower, you're getting warm, moist air. Next slide, please.

So, how much water is used in the cooling tower? You have three major areas of use. So, again, if you're doing that system, that water balance, here's some ways you might be able to estimate how much water you're using in your cooling tower. A couple of rules of thumb, for every ton of cooling, and it think it's like 10 degrees across the condenser, you have 3 GPM of water being used; 1.8 of that is for consumptive uses. So, 1.8 is going to be made up of make-up water, and that's really going to be your water use, so to speak.

There's drift; so that's if you're operating your fans way too hard, and they're pulling water out of there. That could represent a loss. Often, it's very minimal. Then you have blowdown. So, as the sump accumulates more contaminants, you're going to want to dump all the water in the sump and replenish, and that's called blowdown. That's going to be based on your cycles of concentration, which we'll talk about a little bit. The sum of all these equals the total water use, and that's replenished through make-up water. Next slide, please.

So, how much water would these cooling towers entire use? Here's an example of a 100-ton tower using 2 cycles of concentration. So, that's the blowdown. The conductivity of the sump is twice the conductivity of the make-up water, and conductivity is just a measure of how much junk [break in audio] contaminants is in the water. So, in this case, there's 360 gallons-per-hour make-up water to account for the evaporation blowdown. Let's say drift is 0. That equates to this tower – if it's only on half a year – that equates to 1.5 million gallons of water per year. So, it could be a lot of water in your cooling tower. Next slide.

A lot of water reduction opportunities. I think the first thing you think about: Do you need to operate so cold? Do you need so much cooling in your facility or your process? Every ten degrees you can raise that condenser temperature, that's 1.8 gallons per minute you're saving. You're also saving on energy. Every degree you that you increase the condenser temperature is a 2 percent reduction in energy use. So, if you're cooling required through cleaning heat transfer surfaces that's ways to save on water.

Increase the cycles of concentration, get to that. Ensure your fill isn't broken or rotted out. We'll see that pretty often where the airflow is now – either the water is not trickling properly. It's more like dumping down, and the air and the water interface isn't really happening. That's going to affect your cooling rates. So, replace broken or rotten fill. The other thing is there's sump doors; there's access doors. Make sure those are closed so that all the air is directed through the fill and not through other avenues.

The air cool towers, which are more expensive; they're less energy efficient, but they don't use water. So, if you're out in the desert of Arizona or something like that, then maybe that's for you and something you can look at. Cycles of concentration. So, example, if we took that two cycles of concentration example, and we increase it to five, which is a common area where we're seeing some of our partners operate their cooling towers, that's going to be 38 percent reduction in water. So, how can you do this? You can install connectivity meters on your sump. You can automate blowdown at the depth five cycles; then it blows down automatically.

You can also add chemical treatment to your sump. The trade-off there is that you've got to talk to your EHNS people. Is it something you want to do? But that can help you increase your cycles of concentration. Next slide.

Energy use in cooling towers; it's really dominated by two things, the tower fan and the condenser water pumps. The condenser water pumps really aren't part of this cooling tower, but I'm including it here for my purposes. You do get a 500-ton chiller operating at the ASHRAE minimum standard efficiencies, and it's water cooled, 15 percent of the energy is for the cooling tower. Just a rule of thumb there. Well, 8 percent for the fan, 7 percent for the condenser pump. Next slide, please.

A lot of energy-saving opportunities. The next slide highlights some of the fan resources the DoE has, but one thing I want to introduce, if you have multi-cell towers with multiple or multiple towers, and they all each have their own fan, it's better to operate all of them at some lower load with a VFD than it is to operate some on and some off. So, as an example, if you're running 4 fans – if you have a 4-cell tower with four fans, it's better to operate four of the fans at 56 percent low than 2 fans on and 2 fans off.

Then you're going to see a 60 percent reduction in energy consumption and have the same water temperature to your condenser. Of course, your fans have to be fitted with VFDs to realize this. Next slide please.

So, fan system resources from DoE. Again, DoE has been developing many system resources over the years, fans included. There's a software tool, the Fan System Assessment Tool. Literature again. There's a sourcebook and case studies, and again, there's the availability of training through experts or online.

All right, steam systems. So, steam systems, I'm not sure how many of you have steam systems. We'll walk through this a little bit quickly, but it is a large use in the U.S. industry; 31 percent of energy and 11 percent of water use for manufacturing is for steam. Next slide, please.

Walking through a really basic steam system here. Water is sent to a boiler, which is the water has been heated up with some sort of fuel, maybe natural gas and air. It turns into steam. It's distributed throughout the plant and used at some end uses. Dispensed steam is returned as condensate. It might have to be flashed to get back to water. Sent to a deaerator tank. Boiler steam is then sent to the deaerator tank to de-gas the water, and that same condensate is then returned to the boiler. That's a pretty generic description of a steam system, but if you go to the next slide, in that steam system that we just talked about, where are you using water?

So, blowdown, again, is very similar to the cooling tower concept. There's contaminants that accumulate over time, and you're going to have to blowdown the water. So, typically, blowdown is 4 to 8 percent of the boiler feed water flow rate, but it can be as high as 10 in situations where it's not really controlled. So, there's going to be condensate loss. So, if you're not returning all your condensate, then you're essentially sending hot water down the sewer, bringing in make-up water that's cold, and you're going to have to recover all that heat. I shouldn't say recover. You're going to have to re-heat all that water when you could have just returned the condensate.

So, you can't get all your condensate back, but if you can get to 75 to 80 percent, that's great. Then these steam leaks, these are often – they can be through pipes or at the steam traps. Pipes is a little bit less often than steam traps. Steam traps can fail open or fail closed. So, if you have open failed traps, which means essentially their purpose is to separate condensate from steam, but they're just sending steam out rather than just the condensate that's failed open. So you're going to see a significant amount of steam loss there.

The deaerator tank also takes a little bit of steam, and that's much ado about nothing there a little bit. Now, the sum of all these things is make-up water.

So, we put together just a kind of fictitious little balance to show you some of the opportunities here. Here is a steam system that's pulling in 55 million gallons of make-up water a year to produce 100,000 pound-per-hour, 150 PSI steam. This system, we'll say, 30 percent of their traps are failed open; 60 percent recovery is condensate. So, they're sending 40 percent down the drain. They've got 10 percent blowdown, and they have some steam in their deaerator. Let's go to the next slide, please.

Let's say they take that condensate recovery, and they go from 60 percent to 75 percent. Right there, they could save in the next expel, 15 million gallons of water per year, and $75,000.00 in water and sewer charges. Now remember, that condensate is hot water going back to the boiler that then is reheated to make steam as opposed to city water, which might be at 60 degrees. That has to be heated all the way up to steam temperature. So, there's a lot of energy savings. In fact, that's what people usually talk about condensate recovery, but so it's 47,000 BTUs in this case and about $180,000.00.

I want to highlight here that people talk about energy savings, but there are water savings. Excuse me. There's also chemical treatment that you're going to be offsetting. Next slide, please. To reduce our blowdown from 10 percent to 5 percent – 5 percent is a reasonable number to get to – you could use blowdown control, measuring the conductivity, and then blowing down whenever it hits a certain conductivity. But just in that 5 percent reduction or having the blowdown rate, there's 6 million gallons of water, which is $31,000.00. Again, there's the same sort of energy savings or same sorts of energy savings that you don't have to re-heat that water, and you can see energy savings there. Next slide, please.

Now, fixing steam traps through perhaps implementing Steam Traps Inspection Program, you can do that visually. You walk around your plant. You see steam leaks. Temperature shoot it with a gun, with an IR gun, and if it's cold, it's broken – or just listening to these steam traps, leaks and fixing those if they break. We know that this facility can get their broken steam traps down from 30 to 10 percent. You can see the water and energy savings there. So, it's pretty significant, 1.6 million gallons of water and 20,000 MMBTS of energy because they're rounded.  Next slide, please.

So, in all, if this facility did those three sort of basic tune-ups on their boiler, they could reduce their water use by 40 percent, and also see substantial energy and cost savings. We often talk about the cost savings. I just want to highlight there are a lot of water savings in boilers, and there is financial payoff. _____ the chemical treatment cost for the water here, which would also be added. Next slide, please.

So, that same steam system that we showed before, this is what it would look like now. We went from some 50 million gallons per year to 32 million gallons per year make-up water. Next slide.

Speaking of resources again, there's a steam system model there from DoE. There's a whole host of literature. There's a sourcebook, tip sheets, case studies, technical publications, textbooks that are out there. We've got some really qualified folks on steam systems. The good thing about steam is its properties really haven't changed since the 1800s, so all those literature is really relevant today as it will be tomorrow. There's a list of qualified specialists that can come in and help you out with your steam system.

So, I want to pause there. We're almost at the end, and I appreciate folks for hanging on a little bit extra, but pause for any questions.

Bruce Lung:	Okay, well, let's just keep going. I think there's some good tools here.

Prakash Rao:	Sure. So, Bruce, if you could actually hit a couple times more, there's some animations here. I apologize or that. So, the Global Water Tool, I described a little bit with Alissa, to Alissa's question. We see a lot of our partners using this tool. It's the World Business Council for Sustainable Development's Global Water Tool. I want to highlight tools here. We highlighted DoE resources that can help you on the system and energy and water. I want to highlight some tools that can help you that are outside the DoE world that have been developed by some very reputable groups that could really help you tackle things like scarcity and risk and water balances.

One of these tools is the Global Water Tool. We mentioned it earlier. It's really for a corporate manager, but it helps you look at your sites and say, "Which ones are in these really risky areas?" Again, UTC is an advocate of this tool and it was developed with a lot of company input. So, you understand the needs of potential water availability and quality risks at a high level, at the global level. The ten steps are fairly easy to use. Bruce, if you go to the next slide – sorry, I guess there's a few more animations there.

It ties really well in with this Global Water Tool, which was produced by the GEMI, which I think is the Global Environmental Management Initiative. So, the Global Water Tool allows you to see all your facilities, which are the ones that are most at risk in terms of water scarcity. So, water scarcity, I know I've been using that term, is what water is used and is available? That's the way to look at it. The Global Water Tool then says, "All right, I'm going to drive it a little bit deeper into each of those facilities, and I want to provide a little bit more data on how I use water, how much water I use at these facilities, what types of water, how much I'm storing," and get a much better risk assessment at the facility level.

So, water is really driven by – a lot of water conservation efforts are driven by risk, and these two tools can really help you identify those facilities that are at risk and how much at risk are they? So, I wanted to highlight those. The links are right available there. Next slide, please.

Now, a little bit different, more for the water, the facility manager, there's Collecting the Drops. So, a water sustainability planner tool by GEMI. This is at the facility level, and there's a lot of little modules in this tool. It's pretty cool. There's water balances. There's rules of thumb you can follow for doing your water balance on equipment level. There's case studies you can see a lot of companies are doing. It's all global, but it's all water so it just the same everywhere. Also, it does help you with your water management risk assessment as well. It's available at that link over there. If you go to the next slide, please?

So, we want to – the Corporate Water Management white paper that we described, coming out of the Better Buildings, Better Plants Water Savings Initiative, we listed in the back there a whole bunch of tools. We're just highlighting a few here. You'll find all these tools, books, resources, organizations that can help you with water, including the DoE in that white paper. Here we want to just kind of parse it out a little bit for you if you're a facility manager, if you're a corporate sustainability manager, what really works for you, what tools would be great.

If you're looking for the facility manger list, if you're looking for site water risks, the GEMI tools are great. If you're looking to implement your water program, North Carolina's Department of – I forgot what the ENNR stands for again – has a Water Efficiency Manual for CII. A lot of great examples there of measures on how to implement a water efficiency program. A lot of highlights from North Carolina. We often think water is a California issue, but North Carolina has got some great resources.

Those Site Water Added tools, Environmental Defense Fund has a Cooling Tower Efficiency Guide, which was developed with AT&T, which might help you with your cooling towers. For corporate sustainability managers, there's several tools out there to understand water risk across your portfolio including the World Business Council Tool. World Resources Institute has another great tool, The Aqueduct Tool, which helps you look at surface water stress.

There's a financial business case. We haven't talked too much about that, but a couple of tools, Water Risk Monetizers from Ecolab, which helps you understand how much production is at risk or how much revenue, I guess, is at risk with water situations. EDS has more cooling tower tools there as well. Well, that's it, and I'll end it here, and it'll pass it back to Bruce to close it.

Bruce Lung:	Great. Thanks a lot, Prakash. I think that was really a lot of good information, and we hope that this has been valuable for everyone on the phone. We do have a little bit of time in case there are some additional questions that have come up in peoples' minds. So, if there's anything feel free to ask us now. Okay. We do have the contact information for the principle people here at the Better Plants Program for you, and we've also included Prakash's contact information here. Let me just ask, Alissa, how do you expect to be able to use this information for Honda and also for your suppliers?

Alissa:	I'm sorry. It cut out. Did you say how are we going to use this information?

Bruce Lung:			Yes.

Alissa:	So, right now, this was a learning piece for pretty much everyone on the phone, Lisa, Meicheck, and I included. What I would like to do is hopefully, we'll have one or two suppliers join you in, I guess, the Better Plants situation for the water. Then, as a team, we can go together, establish targets, do everything that was outlined today together so that we can learn. Then in the next year or two, start to roll this out to the supply base as we have done energy.

Bruce Lung:	Okay, excellent. So, what we'll do is, like I said, once this is – we finish this – we're recording the webinar, number one. So, you'll be able to hear the recording. Also, this will be turned into a PDF file, so you can share it with your suppliers as well as other stakeholders.

Alissa:	Yeah, and one thing too for anyone on the line that's a supplier, if you're interested in going down this path with Better Plants, I don't know if this is a, I guess, something to entice you, but we do a symposium in October. So, if a supplier does go down this path with Better Plants, I would love to highlight that at the symposium and kind of start to roll this out. It would give the supplier recognition. It gives Better Plants recognition, and then lets the supply base know that North America and Honda North America cares about water.

Bruce Lung:	That's a good point. Thank you.

Alissa:	Okay? So, that's kind of what I'm thinking next steps, but we really do – Honda North America does want to team up with Better Plants – Better Buildings, Better Plants for this first initiative with a handful or one or two suppliers.

Bruce Lung:	Great, okay. Yeah, I think most likely if it's one or two suppliers, and they're already in the program, you can work with Wade. If some folks are outside of it, let's talk offline, and we'll figure out a solution.

Alissa:	Thank you so much. Thank you very, very much for your time today and everyone that joined in and listened.

Bruce Lung:	All right. Prakash, any parting thoughts?

Prakash Rao:	No. My contact information is there, and as Bruce mentioned, there's a few ways to reach out to us. I'm more than happy to help I really appreciate the time today, and I congratulate you, I guess, on just being even on the webinar and being interested in water. I think it shows some really advanced thinking, and that's great to see.

Bruce Lung:	Great. Thanks a lot, Prakash.

Prakash Rao:	Thank you.

Bruce Lung: 	Thanks, everyone. Have a great day.

Alissa:	Bye.

[End of Audio]